Text for specification

Description
AMBUS®Panel
holder for cylindrical fuses, with LED
22 x 58 / 1P
100 A / 110 - 690 V

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
CSA, UL, CCC

Electrical data
Rated current (IEC):	100 A
rated voltage (IEC) AC:	690 V

rated current (UL):	80 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	3.5 W

rated isolation voltage Ui AC:	690 V
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) AC:	725 V

SCCR:	100 kA

for fuse links as per IEC / EN 60269-2 with permitted rated power dissipations
up to max. 9.5W for gG/gL 
up to max. 7W for aM

indicator light
operating voltage range: 110 - 690V AC / DC

Terminal points
box terminal :
4 - 50 mm² / AWG 10 - AWG 1/0 
flexible cables, directly or with wire-end ferrule
Md 3,5 - 4,0 Nm / 31 - 35 lb.in.

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
large clamping range

Brand 
Woehner or equivalent

Part No.
31140000