Text for specification

Description
QUADRON®60Classic
NH fuse switch-disconnector size 1, 250 A
screw M10
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), UL, VDE, CCC

Electrical data
Rated current (IEC):	250 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	250 V

rated current (UL):	250 A
rated voltage (UL) AC:	600 V

AC-22B (400 V)
AC-23B (400 V / 160 A)
AC-21B (500 V)

to obtain a higher utilisation category the product can be retrofitted with arcing chambers (see accessories)

power dissipation at full load of the item:	26.0 W

rated isolation voltage Ui AC:	690 V
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) AC:	725 V
max. permitted voltage (IEC) DC:	262 V

rated peak withstand current  Ipk max.:	13.7 kA

SCCR:	100 kA

for fuse links IEC 60269-2-1 (I) / DIN VDE 0636-201 size 1 up to 23W power dissipation, with grip lugs under voltage

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.
Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich.

Schutzart IP30 frontseitig, im Anschlussbereich vom Einbau abhängig

Elektronische Sicherungsüberwachung:
- Zur Erkennung von Sicherungsausfällen mit Bemessungsspannung AC 100V bis AC 690V
- Keine Hilfsenergie erforderlich; Versorgung über Netzspannung
- Hilfskontakte potentialfrei
- LED- Blinkmelder (rot/grün)
- Testtaster
- Weitere Informationen unter Downloads / Datenblatt

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other
Self-closing test holes are available in the cover.

Brand 
Woehner or equivalent

Part No.
33325000