Text for specification

Description
QUADRON^®100Energy
NH in-line fuse base, 160 A
wedge terminal 70 mm²
size 00
100Energy

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V

power dissipation at full load of the item:	17.5 W
rated surge voltage U_imp :	6 kV
max. permitted voltage (IEC) AC:	800 V
short-circuit strength when protected by fuses:	50 kA

Terminal points
wedge clamp terminal for Cu an Al:
stranded round 16 - 70 mm²,
stranded sectored 16 - 70 mm²,
flexible with wire-end ferrules 16 - 70 mm²

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
Undrilled mounting possible with terminal clamp

Brand 
Woehner or equivalent

Part No.
33384000