Text for specification

Description
universal busbar support
3-pole with internal screw holes
60Classic

Standards
IEC 61439-1:2011

Electrical data
rated voltage (IEC) AC:	690 V

rated isolation voltage U_i AC:	1000 V
rated surge voltage U_imp :	8 kV
max. permitted voltage (IEC) DC:	1500 V

short-circuit capacity IEC / EN :
Ipk max. = 80 kA (busbar 30x10, 2 busbar supports in 250 mm distance)

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Screws:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
With internal screw holes
can also be used as centre support

Brand 
Woehner or equivalent

Part No.
01603000