Text for specification

Description
SECUR®Panel
switch-disconnector for D0 fuses up to 63 A
3P + N

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
VDE, CCC

Electrical data
Rated current (IEC):	63 A
rated voltage (IEC) AC:	400 V
rated voltage (IEC) DC:	130 V

AC-22B

power dissipation at full load of the item:	9.0 W

rated isolation voltage Ui AC:	500 V
rated surge voltage Uimp :	6 kV

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638 : AC-22

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

Miscellaneous 
Double function terminal
any feed direction
captive fuse-carrier
sealable operation

Brand 
Woehner or equivalent

Part No.
31315000A