Text for specification

Description
EQUES®60Classic
busbar adapter 25 A
for direct starter Siemens S00 with spring terminal connection
45 x 200, with 165 mm long leads AWG 12 (4 mm²)
60Classic

Standards
IEC 61439-1:2011

Approvals
CSA, UL

Electrical data
Rated current (IEC):	25 A
rated voltage (IEC) AC:	690 V

rated current (UL):	25 A
rated voltage (UL) AC:	600 V

power dissipation at full load of the item:	1.9 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV

SCCR: 30 kA with 3RV20 12,5 A / 600 V AC, 65 kA with 3RV20 16 A / 480 V AC, 65 kA with 3RV20 25 A / 480 V AC, 50 kA with 3RV20 32 A / 480 V AC 

Miscellaneous 
Leitungsenden ultraschallverdichtet.
Rastmechanismus beim Aufschieben auf die Sammelschiene.
Extra lange Leitungen für die Cage-Clamp-Anschlüsse

Brand 
Woehner or equivalent

Part No.
32650000