Text for specification

Description
CRITO^®60Classic
connection set, 4-pole, without cover
95 -  300 mm², AWG 3/0 - 600 MCM
60Classic

Standards
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Approvals
UL

Electrical data
Rated current (IEC):	500 A
rated voltage (IEC) AC:	800 V

rated current (UL):	420 A
rated voltage (UL) AC:	600 V
current capacity (IEC) max.:	560 A
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  I_pk max.:	50.3 kA

SCCR: 65 kA with any DIVQ/7 circuit breaker 400 A / 480 V AC, 35 kA with any DIVQ/7 circuit breaker 400 A / 600 V AC, 200 kA with fuse JDDZ Class J 600 A / 600 V AC, 200 kA with JDDZ fuse Class L 800 A / 600 V AC, 100 kA with JDDZ fuse Class L 1200 A / 600 V AC 

Terminal points
Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200

Terminals: 	galvanised steel, chromited screw: 	hexagon socket screw, galvanised, chromited, thrust piece 	brass, nickel-plated

Brand 
Woehner or equivalent

Part No.
01147000