Text for specification

Description
AMBUS®60Classic
busbar mounted fuse holder 1000 V
for fuses 10x38 IEC 60269-6
1-pole, for busbars 20 x 5/10 
60Classic

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Approvals
UL, CCC

Electrical data
Rated current (IEC):	30 A
rated voltage (IEC) DC:	1000 V

rated current (UL):	30 A
rated voltage (UL) DC:	1000 V

power dissipation at full load of the item:	0.2 W
max. permitted voltage (IEC) DC:	1050 V

SCCR:	33 kA

for fuse links as per IEC 60269-6 
gPV with power dissipation up to max. 4W

Terminal points
cage clamp connection
screw drive: PZ2 
wire stripping: 11 mm
min. cross-section: 0.75 mm²
max. cross-section: 25 mm²
cage clamp connection
screw drive: PZ2 
wire stripping: 11 mm
min. cross-section: 0.75 mm²
max. cross-section: 25 mm²
Md min.: 2.0 Nm
Md max.: 2.5 Nm
Not suitable for aluminium cables !

Brand 
Woehner or equivalent

Part No.
31572000AB