Text for specification

Description
in-line fuse switch-disconnector 160 A
screw M8 / clamp 70 mm², with electronic fuse monitoring
size 00
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), CCC

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	400 V

AC-23B (400V)

power dissipation at full load of the item:	20.0 W

rated isolation voltage Ui AC:	400 V
rated surge voltage Uimp :	4 kV

Electronic fuse monitoring:
nominal voltage: 3AC 400V,
nominal frequency: 50...40Hz,
switch contact: 2 changeover switches, max. AC 250V, AC15  closer 3A, opener 1A,
rated surge voltage: 4kV,
pollution degree: 2

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Terminal points
screw M8 : 
Md 12 - 14 Nm

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Contacts:
	spring-loaded copper contacts, silver plated 
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
Self-closing inspection holes are available in the cover.
Electronic fuse monitoring:
operating current principle, optionally with latching properties (latches without bridge X1-X2)
device display:
green LED = intact fuses
red LED = fuse tripped, cover position up

Brand 
Woehner or equivalent

Part No.
33285000