Text for specification

Description
CRITO^®185Power
connection module
for lam. Cu max. 2x 80 x 10
without cover
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Standards
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Approvals
UL

Electrical data
Rated current (IEC):	1,400 A
rated voltage (IEC) AC:	690 V

rated current (UL):	1,400 A
rated voltage (UL) AC:	1000 V
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  I_pk max.:	84.6 kA

the following short-circui values can be reached, if the phase distance of the connection modules is extended from 100mm to 150mm :
Ipk : 107 kA
Icw : 50,7 kA / 1s

Miscellaneous 
also rigid copper busbars can be connected if they are installed without mechnical tension 

Brand 
Woehner or equivalent

Part No.
01442000A