Text for specification

Description
QUADRON^®Panel
NH fuse-base 160 A
both sides clamp
size 00 / 1P, with touch protection

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	440 V

power dissipation at full load of the item:	4.2 W
rated surge voltage U_imp :	6 kV
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1000 V
short-circuit strength when protected by fuses:	50 kA

Miscellaneous 
For safe connection of the leads, the shock protection is split into 2.

Brand 
Woehner or equivalent

Part No.
03760000