Text for specification

Description
CrossBoard®
basic system 160 A
3-pole
1000 mm long, touch-safe protected

Standards
IEC 61439-1:2020

Approvals
IEC (CB), UL

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V

rated current (UL):	160 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) DC:	800 V

rated peak withstand current  Ipk max.:	30 kA

SCCR: 100 kA with JDDZ fuse Class J 400 A / 600 V AC, 65 kA with any DIVQ/7 circuit breaker 400 A / 480 V AC 

Miscellaneous 
touch-safe protected busbar system up to 160 A
rear feedable
plug and play
easy to screw to mounting plates
completely pre-assembled and immediately ready for use

Brand 
Woehner or equivalent

Part No.
11000000A