Text for specification

Description
EQUES®185Power
busbar adapter 800 A
300 x 652, connection top, clamp connection 
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Standards
IEC 61439-1:2011

Approvals
UL

Electrical data
Rated current (IEC):	800 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	800 V

rated current (UL):	800 A
rated voltage (UL) AC:	1000 V

power dissipation at full load of the item:	176.0 W

rated isolation voltage Ui AC:	1000 V
rated surge voltage Uimp :	12 kV

rated peak withstand current  Ipk max.:	106 kA

Brand 
Woehner or equivalent

Part No.
32767000A