Text for specification

Description
CRITO^®
brace terminal
Cu / Al 95 - 185 mm²
60Classic
100Energy
185mm-System
centre feed unit

Standards
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Approvals
UL

Electrical data
Rated current (IEC):	300 A
rated voltage (IEC) AC:	690 V

rated current (UL):	310 A
rated voltage (UL) AC:	600 V
current capacity (IEC) max.:	500 A
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  I_pk max.:	55,8 kA

SCCR:	25 kA

Terminal points
for applications acc. to IEC / EN :
Cu or Al 95 - 185 mm² stranded round cables and stranded sectored cables
Cu also flexible cables, directly,

for applications acc. to UL / CSA :
Cu 95 - 185 mm² / AWG 3/0 - MCM 350
Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Material properties
Connecting screws:
	Set screw M16, Allan key size 8
Terminal body:
	steel, galvanized and chromized
cable base:
	brass, tin plated

Terminal body: 	galvanised steel, chromited screw: 	hexagonal socket screw M16 x 1.5 (S8), galvanised, chromited, cable bed: 	brass, nickel-plated

Miscellaneous 
Terminal with captive clamp screws, conductor can be overlapped, indication of nominal cross-section and tightening torque noted on the terminal, contact between conductor and busbar via cable bed.

Brand 
Woehner or equivalent

Part No.
01318000