Text for specification

Description
universal busbar support
2-pole with internal screw holes
60Classic

Standards
IEC 61439-1:2011

Electrical data
rated voltage (IEC) AC:	800 V
rated voltage (IEC) DC:	1000 V

rated isolation voltage U_i AC:	1000 V
rated surge voltage U_imp :	6 kV
max. permitted voltage (IEC) DC:	1500 V

Short-circuit withstand capacity:
Icw up to 39.8kA - 255ms - DC busbar support separation 250 mm (20 x 10 mm busbars)
Icw up to 45.7kA - 255ms - DC busbar support separation 400mm (30 x 10mm busbars)

Miscellaneous 
With internal screw holes
can also be used as centre support

Brand 
Woehner or equivalent

Part No.
01602000