Text for specification

Description
QUADRON®Panel
NH fuse-base 600 A, panel mounting, for PV
both sides screw M12
size 2XL / 3L, 1P, with touch protection

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Electrical data
Rated current (IEC):	600 A
rated voltage (IEC) AC:	1000 V
rated voltage (IEC) DC:	1500 V

rated current (UL):	600 A
rated voltage (UL) DC:	1500 V

power dissipation at full load of the item:	13,8 W
rated surge voltage Uimp :	6 kV
short-circuit strength when protected by fuses:	50 kA

SCCR:	15 kA

for fuse links IEC 60269-6

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Connecting screws:
	screw M12, galvanized, chromized
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
For safe connection of the leads, the shock protection is split into 2.

Brand 
Woehner or equivalent

Part No.
03294000