Text for specification

Description
CAPUS®Panel
switch-disconnector 3-pole
screw M10, red handle
250 A

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB)

Electrical data
Rated current (IEC):	250 A
rated voltage (IEC) AC:	500 V

AC-23A (500A/200A)
AC-23 B (415V)
AC-22 B (500V)
AC-21 B (500V)

power dissipation at full load of the item:	33,5 W

rated isolation voltage Ui AC:	1000 V
rated surge voltage Uimp :	12 kV
rated making capacity:	20 kA

conv. therm. current in housing
250 A, horizontal installation (adjacent poles) encapsulated 252 x 378 x 302mm
250 A, vertical installation (poles beneath each other) encapsulated 300 x 400 x 200 mm

max. rated operating voltage 500V AC
max. rated operating current   250A
current type AC (50-60Hz)
rated insulation voltage 1000V
rated surge voltage strength 12kV
short-time current strength   7kA -1s
rated conditional short-circuit current 80/50kA (fuses gL/gG; size 1 -200/250A-500V)
mechanical lifespan (switching operations) 7000
rated short-circuit making capacity 20kA

Terminal points
screw M10 :
Md 25 - 31 Nm

Miscellaneous 
double-breaking main contacts, 
visible separation sections, 
user-independent switching, 
assembly and connection material contained in scope of delivery

Brand 
Woehner or equivalent

Part No.
33355000