Text for specification

Description
busbar support
3-pole, with internal screw holes
60Classic

Standards
IEC 61439-1:2011

Approvals
CSA, UL

Electrical data
rated voltage (IEC) AC:	800 V
rated voltage (UL) AC:	600 V

rated isolation voltage Ui AC:	1000 V
rated surge voltage Uimp :	8 kV
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  Ipk max.:	90 kA

short-circuit capacity IEC / EN :
Ipk max. = 90 kA (2 busbar supports in 500 mm distance)
go to calculation for  3-pole system (IEC)   

Miscellaneous 
Suitable as outer and centre supports
with internal screw holes.

Brand 
Woehner or equivalent

Part No.
01232000