Text for specification

Description
CRITO®
brace terminal
Cu / Al 95 - 300 mm²
60Classic
100Energy
185mm-System
centre feed unit

Standards
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Approvals
CSA, UL

Electrical data
Rated current (IEC):	500 A
rated voltage (IEC) AC:	690 V

rated current (UL):	420 A
rated voltage (UL) AC:	600 V
current capacity (IEC) max.:	600 A
max. permitted voltage (IEC) AC:	1000 V
max. permitted voltage (IEC) DC:	1500 V

rated peak withstand current  Ipk max.:	81,4 kA

SCCR:	65 kA

Terminal points
for applications acc. to IEC / EN :
Cu 95 - 300 mm² stranded round cables and stranded sectored cables as well as flexible cables (directly)
Cu 240 - 300 mm² fine stranded flexible cables (directly)
Al 120 - 300 mm² stranded round cables and stranded sectored cables
Al 120 - 240 mm² solid sectored cables

for applications acc. to UL / CSA :
Cu 95 - 300 mm² / AWG 3/0 - MCM 600

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Brand 
Woehner or equivalent

Part No.
01760000