Text for specification

Description
QUADRON®Panel
NH fuse-base 600 A, panel mounting, for PV 
incoming connection screw M10, outgoing connection to busbar 2x 40 x 10
size 2XL / 3L, 1P, with touch protection

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Electrical data
Rated current (IEC):	600 A
rated voltage (IEC) AC:	1000 V
rated voltage (IEC) DC:	1500 V

rated current (UL):	600 A
rated voltage (UL) DC:	1500 V

power dissipation at full load of the item:	13,8 W
rated surge voltage Uimp :	6 kV
short-circuit strength when protected by fuses:	50 kA

SCCR:	15 kA

Bei praxisgerechter Anordnung muss bezüglich Strombelastbarkeit, bezogen auf den Nennstrom der Sicherung, ein Reduktionsfaktor von 0,6 berücksichtigt werden.

for fuse links IEC 60269-6

Miscellaneous 
For one or two internal busbars 40x10mm.
Busbar fully shock protected by the contact cover.
The shock protection is split into 2.

Brand 
Woehner or equivalent

Part No.
03293000