Text for specification

Description
QUADRON^®60Classic
NH busbar mounted fuse base 400 A
screw M10
size 2 / 3P
60Classic

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Electrical data
Rated current (IEC):	400 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	440 V

power dissipation at full load of the item:	56,0 W
rated surge voltage U_imp :	6 kV
max. permitted voltage (IEC) AC:	800 V
max. permitted voltage (IEC) DC:	800 V
short-circuit strength when protected by fuses:	50 kA

Brand 
Woehner or equivalent

Part No.
03693000