Text for specification

Description
AMBUS^®Panel
holder for cylindrical fuses, for semiconductor fuses
22 x 58 / 3P
100 A / 690 V

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), CSA, UL, CCC

Electrical data
Rated current (IEC):	100 A
rated voltage (IEC) AC:	690 V

rated current (UL):	80 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	10,5 W

rated isolation voltage U_i AC:	800 V
rated surge voltage U_imp :	6 kV

SCCR:	100 kA

for fuse links as per IEC / EN 60269-2 with permitted rated power dissipationsup to max. 9.5W for gG/gL up to max. 7W for aMfor fuse links aR / gR / gRL under operation conditions up to max. 11W, for which at least 50mm² leads must be connected

Terminal points
box terminal :
4 - 50 mm² / AWG 10 - AWG 1/0 
flexible cables, directly or with wire-end ferrule
Md 3,5 - 4,0 Nm / 31 - 35 lb.in.

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
large clamping range

Brand 
Woehner or equivalent

Part No.
31283000