Text for specification

Description
comb-type busbar, 2-pole, bridge type, pitch 18 mm
100 A, 1 m long
25 mm²
Accessories

Standards
IEC 61439-1:2011

Approvals
UL

Electrical data
Rated current (IEC):	100 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	600 V

rated current (UL):	100 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	2,8 W
current carrying capacity for centre feed:	200 A
rated surge voltage Uimp :	4 kV

SCCR: 100 kA with fuse Class J 200 A 

UL / CSA :
 480V AC, with AES CC or AES 10x38 also 600V AC
 100A for side feed
 200A for centre feed

 SCCR = 10kA
 SCCR = 100kA for Class J 200A fuse

Brand 
Woehner or equivalent

Part No.
31561000