Text for specification

Description
EQUES®60Classic
busbar adapter 45 A
2 adjustable mounting rails
54 x 260, with removable upper section and leads AWG 8 (10 mm²)
60Classic

Standards
IEC 61439-1:2011

Approvals
CSA, UL

Electrical data
Rated current (IEC):	45 A
rated voltage (IEC) AC:	690 V

rated current (UL):	45 A
rated voltage (UL) AC:	600 V

power dissipation at full load of the item:	5,5 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV

SCCR: 65kA with any DIVQ/7 circuit breaker 40A / 480V AC 

Miscellaneous 
Conductor ends ultrasonically sealed.
Click mechanism when pushing onto the busbar.

Brand 
Woehner or equivalent

Part No.
32416000