Text for specification

Description
QUADRON^®60Classic
NH fuse-switch-disconnector size 00, 160 A
screw M8
suitable for 5-pole system
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), UL, VDE, CCC

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	440 V

rated current (UL):	160 A
rated voltage (UL) AC:	600 V

power dissipation at full load of the item:	17,7 W

rated isolation voltage U_i AC:	800 V
rated surge voltage U_imp :	6 kV
max. permitted voltage (IEC) DC:	800 V

SCCR:	100 kA

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.

Bei Dauerbetrieb von mehreren Geräten nebeneinander ist der Bemessungsbelastungsfaktor nach VDE 0660 Teil 500 / EN60439-1, Tabelle 1 zu beachten.

System component: degree of protection IP30 at front as per DIN EN 60529, degree of protection near terminal depends on installation
adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Terminal points
Schellenanschluß (im Lieferumfang enthalten): Cu 1,5 -70mm² rm, f+AE; lam. Cu 12x1-10;
3 Nm Drehmoment

Brand 
Woehner or equivalent

Part No.
33079000