Text for specification

Description
QUADRON®Panel
NH fuse switch-disconnector size 00, 160 A, panel mounting
clamp 70 mm²

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), UL, CCC

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	250 V

rated current (UL):	160 A
rated voltage (UL) AC:	600 V

AC-23B (400 V),
AC-22B (500 V),
AC-21B (500 V

power dissipation at full load of the item:	7,0 W

rated isolation voltage Ui AC:	690 V
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) AC:	725 V
max. permitted voltage (IEC) DC:	262 V

SCCR:	100 kA

for fuse links IEC 60269-2-1 (I) / DIN VDE 0636-201 size 00 up to 12W power dissipation, with grip lugs under voltage

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.
Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich.

Schutzart IP30 frontseitig, im Anschlussbereich vom Einbau abhängig

Elektronische Sicherungsüberwachung:
- Zur Erkennung von Sicherungsausfällen mit Bemessungsspannung AC 100V bis AC 690V
- Keine Hilfsenergie erforderlich; Versorgung über Netzspannung
- Hilfskontakte potentialfrei
- LED- Blinkmelder (rot/grün)
- Testtaster
- Weitere Informationen unter Downloads / Datenblatt

Terminal points
clamp-type terminals : 
1.5 - 70 mm² 
flexible cables with wire-end ferrule, 
stranded round cables, 
lam. Cu max. 12 mm wide, max. 10 mm thick
Md 3 Nm

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
self-closing inspection holes are available in the cover, shock protection split into 2 for safe connection

Brand 
Woehner or equivalent

Part No.
33328000