Text for specification

Description
QUADRON^®185Power
in-line fuse switch-disconnector 160 A
Size 00, 3-pole switchable
flat version with box terminal 70 mm²
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), CCC

Electrical data
Rated current (IEC):	160 A
rated voltage (IEC) AC:	800 V

AC-22B (800 V / 63 A)
AC-21B (690 V / 125 A)
AC-22B (500 V / 160 A)
AC-23B (400 V / 160 A)

DC-20B
max. voltage between the fuses: 1000 V
visible information required: Do not switch under load.

power dissipation at full load of the item:	23,0 W

rated isolation voltage U_i AC:	1000 V
rated surge voltage U_imp :	8 kV

Degree of protection IP20 at front, degree of protection near terminal depends on installation

Terminal points
Box terminal:
1,5 -70mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the insulated lead 95mm² could be connectable
1,5 -10mm² solid round
16 -70mm² stranded round
2x10mm², 2x16mm² and 2x25mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square
2x 10-35mm² flexible identical cables placed side by side

lam. Cu. 9-13 mm wide
terminal space 13mm x 13mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
Self-closing inspection holes are available in the cover.
Cover can be locked when closed.

Brand 
Woehner or equivalent

Part No.
33773000A