Text for specification

Description
EQUES®60Classic
busbar adapter 16 A
1 fixed mounting rail, with fuse-carrier 10x38 / Class CC
22.5 x 200, with removable upper section and leads AWG 14 (2.5 mm²)
60Classic

Standards
IEC 61439-1:2011

Approvals
UL

Electrical data
Rated current (IEC):	16 A
rated voltage (IEC) AC:	690 V

rated current (UL):	12,5 A
rated voltage (UL) AC:	600 V

power dissipation at full load of the item:	3,0 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) AC:	725 V

Miscellaneous 
Conductor ends ultrasonically sealed.
Click mechanism when pushing onto the busbar.

Brand 
Woehner or equivalent

Part No.
36003000D