Text for specification

Description
QUADRON^®60Classic
NH fuse base 250 A
screw M10
size 1 / 3P
60Classic

Standards
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Approvals
CCC

Electrical data
Rated current (IEC):	250 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	440 V

power dissipation at full load of the item:	31.4 W
rated surge voltage U_imp :	6 kV
max. permitted voltage (IEC) AC:	800 V
max. permitted voltage (IEC) DC:	800 V
short-circuit strength when protected by fuses:	80 kA

Adapter module, degree of protection IP20 at front

Material properties
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other

Brand 
Woehner or equivalent

Part No.
03301000