Text for specification

Description
SECUR®Panel
switch-disconnector for D0 fuses up to 25 A
3P

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
VDE, CCC

Electrical data
Rated current (IEC):	25 A
rated voltage (IEC) AC:	400 V
rated voltage (IEC) DC:	130 V

power dissipation at full load of the item:	7.8 W

rated isolation voltage Ui AC:	500 V
rated surge voltage Uimp :	6 kV

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

Terminal points
box terminal :
1,5 - 35 mm²    flexible cables, directly or with wire-end ferrule
(flexible cables of maximum cross-section may not fit when using wire-end ferrule)
1,5 - 10 mm²    solid
Md 2,5 - 3 Nm

2 cables can be connected, when both chambers of the terminal are used
the maximum combination is 35mm² + 16mm²

Miscellaneous 
Double function terminal
any feed direction
captive fuse-carrier
sealable operation

Brand 
Woehner or equivalent

Part No.
31532000A