Text for specification

Description
QUADRON Panel
NH fuse switch-disconnector size 00, 160 A, panel mounting
screw M8

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
UL, CCC

Electrical data
rated current (IEC):	160 A
rated voltage (IEC) AC:	690 V
rated voltage (IEC) DC:	440 V

rated current (UL):	160 A
rated voltage (UL) AC:	600 V

AC-21B (690 V)
AC-22B (500 V)
AC-23B (400 V)

power dissipation at full load of the item:	7.0 W

rated isolation voltage Ui AC:	800 V
rated surge voltage Uimp :	6 kV
max. permitted voltage (IEC) DC:	800 V

SCCR:	100 kA

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, the distances to earthed metal parts given below are to be adhered to. - top 150mm, side 55mm
When used as a disconnector, the spacings can be ignored.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Miscellaneous 
For safe connection of the leads, the shock protection is split into 2. Self-closing inspection holes are available in the cover.

Brand 
Woehner or equivalent

Part No.
33200000