Text for specification

Descripción
CRITO^®30Compact
módulo de conexión
con bornes elásticos integrados, 1,5 - 16 mm², AWG 14 - 6
3 polos
30Compact 3P

Normas
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

homologaciónes
UL

datos eléctricos
intensidad de corriente nominal (IEC):	63 A
tensión nominal (IEC) AC:	690 V

intensidad de corriente nominal (UL):	48 A
tensión nominal (UL) AC:	600 V
máxima intensidad de corriente (IEC):	80 A

tensión nominal de aislamiento Ui AC:	800 V
tensión máxima (IEC) AC:	800 V
tensión máxima (IEC) DC:	800 V

resistencia a corriente de pico Ipk máx. :	10 kA

SCCR: 50 kA with JDDZ fuse Class J 60 A / 600 V AC, 35 kA with any DIVQ/7 circuit breaker 60 A / 480 V AC  

puntos de apriete
for leads as per IEC :
Cu 1.5 - 16mm²
round conductor solid or stranded, flexible, direct or with wire-end ferrule

for leads as per UL :
Cu AWG 16 - 6
Class B (UL486E)

cualidad de materiales
Cuerpo principal:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Tapa:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Brand 
Woehner or equivalent

Part No.
01562000A