Text for specification

Descripción
CRITO^®60Classic
placa de bornes de conexión, 3 polos
95 -  300 mm²
60Classic

Normas
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

datos eléctricos
intensidad de corriente nominal (IEC):	500 A
tensión nominal (IEC) AC:	690 V
máxima intensidad de corriente (IEC):	560 A
tensión máxima (IEC) AC:	1000 V
tensión máxima (IEC) DC:	1500 V

resistencia a corriente de pico Ipk máx. :	63.1 kA

puntos de apriete
for applications acc. to IEC / EN :
Cu 95 - 300 mm² stranded round cables and stranded sectored cables as well as flexible cables (directly)
Cu 240 - 300 mm² fine stranded flexible cables (directly)
Al 120 - 300 mm² stranded round cables and stranded sectored cables
Al 120 - 240 mm² solid sectored cables

for applications acc. to UL / CSA :
Cu 95 - 300 mm² / AWG 3/0 - MCM 600

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

cualidad de materiales
Cuerpo principal:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Cubierta:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free

Terminals: 	galvanised steel, chromited screw: 	hexagon socket screw, galvanised, chromited, thrust piece 	brass, nickel-plated

Miscellaneous 
Terminals with captive clamping screws
Conductor can be overlapped
Indication of nominal cross-section and tightening torque noted on the terminals.

Brand 
Woehner or equivalent

Part No.
01754000