Text for specification

Descripción
QUADRON®60Classic
parte inferior de base NH de 250 A, salida parte superior / inferior
tornillo M10
talla 1/3P
60Classic

Normas
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

homologaciónes
CCC

datos eléctricos
intensidad de corriente nominal (IEC):	250 A
tensión nominal (IEC) AC:	690 V
tensión nominal (IEC) DC:	440 V

power dissipation at full load of the item:	31.4 W
tensión de pico Uimp:	6 kV
tensión máxima (IEC) AC:	800 V
tensión máxima (IEC) DC:	800 V
corriente de cortocircuito cuando se protege por fusibles:	80 kA

Adapter module, degree of protection IP20 at front

cualidad de materiales
Cuerpo principal:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contactos:
	spring-loaded copper contacts, silver plated 
Protección contra contacto:
	Resistencia a la temperatura hasta 125°C, 
	autoextintor según UL 94, 
	Resistencia a las corrientes de fuga CTI 200

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other

Brand 
Woehner or equivalent

Part No.
03301000