Text for specification

Descripción
CRITO^®CrossBoard
módulo de conexión
con terminales tipo brida 6 - 50 mm² / AWG 10 - AWG 1
3 polos

Normas
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

homologaciónes
UL

datos eléctricos
intensidad de corriente nominal (IEC):	125 A
tensión nominal (IEC) AC:	690 V

intensidad de corriente nominal (UL):	100 A
tensión nominal (UL) AC:	600 V
máxima intensidad de corriente (IEC):	125 A

tensión nominal de aislamiento Ui AC:	800 V
tensión máxima (IEC) AC:	800 V
tensión máxima (IEC) DC:	800 V

resistencia a corriente de pico Ipk máx. :	15 kA

SCCR: 100 kA with any DIVQ/7 circuit breaker 100 A / 480 V AC, 65 kA with any DIVQ/7 circuit breaker 100 A / 600 V AC, 100 kA with JDDZ fuse Class J 175 A / 600 V AC 

puntos de apriete
6 - 50 mm² / AWG 10 - AWG 1 
feindrähtig, direkt geklemmt oder mit Aderendhülse, 
6 - 35 mm² Rundleiter mehrdrähtig,
(feindrähtig mit Aderendhülse eventuell nicht mit maximalen Querschnitt möglich) 

Miscellaneous 
direct connection to the CrossBoard, cover included

capable of feeding (up to 125 A) 1 or 2 CrossBoards simultaneously with balanced or unbalanced load on the boards.

can be used without cables as a bridge connection between 2 CrossBoards up to 125 A. Feeding a third CrossBoard with cables is acceptable, but the total current cannot exceed 125 A.

touch-safe

CRITO® unlockable from top or bottom

Brand 
Woehner or equivalent

Part No.
01593000A