Text for specification

Descripción
CRITO®CrossBoard
módulo de conexión
brida de 150 mm²
3 polos

Normas
IEC 61439-1:2020
IEC 60999-1:1999
IEC 60999-2:2003

homologaciónes
UL

datos eléctricos
intensidad de corriente nominal (IEC):	320 A
tensión nominal (IEC) AC:	690 V

intensidad de corriente nominal (UL):	285 A
tensión nominal (UL) AC:	600 V
máxima intensidad de corriente (IEC):	320 A

tensión nominal de aislamiento Ui AC:	800 V
tensión de pico Uimp:	6 kV
tensión máxima (IEC) AC:	800 V
tensión máxima (IEC) DC:	800 V

resistencia a corriente de pico Ipk máx. :	40 kA

SCCR: 65 kA with any DIVQ/7 circuit breaker 400 A / 480 V AC, 100 kA with JDDZ fuse Class J 400 A / 600 V AC 

puntos de apriete
Connecting circular conductors: 

35... 50 mm² / 2... 1/0 AWG 

4Nm / 35 lb in

70... 150 mm² / 2/0 AWG... 300 kcmil

6Nm / 53 lb in

35... 95 mm² flexible conductors, circular stranded conductors, flexible conductors with wire-end ferrules DIN 46228-1 max. 30 mm

120... 150 mm² flexible and circular stranded conductors

Connecting flexible conductors:

4x - 10x 15,5mm  x 0,8 mm

6Nm / 53 lb in  

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Brand 
Woehner or equivalent

Part No.
01594000A