Text for specification

Descripción
AMBUS^®Panel
soporte para fusibles cilíndricos, para fusibles semiconductores
10 x 38 / 2P
32 A/690 V, para protección de semiconductor

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
IEC (CB), CSA, UL, CCC

datos eléctricos
intensidad de corriente nominal (IEC):	32 A
tensión nominal (IEC) AC:	690 V

intensidad de corriente nominal (UL):	30 A
tensión nominal (UL) AC:	600 V
tensión nominal (UL) DC:	600 V

AC-22B (400V)

power dissipation at full load of the item:	0.6 W

tensión nominal de aislamiento Ui AC:	800 V
tensión de pico Uimp:	6 kV

SCCR:	100 kA

for fuse links as per IEC / EN 60269-2 
with permitted rated power dissipations
up to max. 3W for gG/gL 
up to max. 1.2W for aM
up to max. 4.3W for aR/gR

puntos de apriete
for applications acc. to IEC / EN :
1 wire: 
Cu 0,75 - 25 mm²
2 wires (of same cross-section): 
Cu 0,75 - 10 mm² 
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E
1 wire: 
AWG 18 - AWG 8, Class B, Md 2,0 -2,5 Nm / 18 - 22 lb.in.
AWG 6 - AWG 4, Class C, Md 2,5 - 3,0 Nm / 22 - 26 lb.in.
2 wires (of identical cross-section): 
AWG 18 - AWG 8, Class B, Md 2,0 - 2,5 Nm / 18 - 22 lb.in. 
AWG 6, Class C, Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

Miscellaneous 
large clamping range
holder for label

Brand 
Woehner or equivalent

Part No.
31276000