Text for specification

Descripción
SECUR®60Classic PowerLiner
D0 interruptor-seccionador con fusibles sobre barras
para los fusibles D01 y D02, con LED
E18 / 63 A / 3P
60Classic

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
VDE, CCC

datos eléctricos
intensidad de corriente nominal (IEC):	63 A
tensión nominal (IEC) AC:	400 V
tensión nominal (IEC) DC:	110 V

AC-23A (400 V)

DC-21B (48V) 1 pole
DC-21B (110V) 2 poles

power dissipation at full load of the item:	10.5 W

tensión nominal de aislamiento Ui AC:	500 V
tensión de pico Uimp:	6 kV

LED indicates blown fuse, operating range: 110 - 400 V AC / DC

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638: AC22

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard.

There is a transfer of the potential from the busbars, through the LED units, to the terminals  when the fuse links are removed and the switching mechanismn is closed. 

Brand 
Woehner or equivalent

Part No.
31525000