Text for specification

Descripción
CAPUS®Panel
seccionador con fusibles, 3 polos
tornillo M10, maneta gris grafito
talla 1

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
IEC (CB)

datos eléctricos
intensidad de corriente nominal (IEC):	250 A
tensión nominal (IEC) AC:	690 V

AC-23B (690V)
AC-22B (690V)
AC-21B (690V)

power dissipation at full load of the item:	45.0 W

tensión nominal de aislamiento Ui AC:	1000 V
tensión de pico Uimp:	8 kV

Mechanical lifespan (switching operations) 7000

conv. therm. current in housing
250 A, horizontal installation (adjacent poles) encapsulated 504 x 378 x 302mm
250 A, vertical installation (poles beneath each other) encapsulated 500 x 500 x 300mm

Shock protection at front with terminal space cover

IP20 for fuse links DIN 43620 size 1 up to 23W power dissipation

puntos de apriete
Tornillo M10 :
Par de apriete 25 - 31 Nm

Miscellaneous 
double-breaking main contacts, visible separation sections, user-independent switching, voltage-free exchange of fuses, assembly and connection material contained in scope of delivery.

Brand 
Woehner or equivalent

Part No.
33338000