Text for specification

Descripción
QUADRON^®185Power
Módulo con 4 Interruptores-seccionadores de fusibles NH, 3 polos
4x NH 000 (max. 63 A)
185Power

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

datos eléctricos
intensidad de corriente nominal (IEC):	252 A
tensión nominal (IEC) AC:	690 V
tensión nominal (IEC) DC:	440 V

AC-21B (690 V / 80 A)
AC-22B (400 V / 125 A)

power dissipation at full load of the item:	103.0 W

tensión nominal de aislamiento Ui AC:	800 V
tensión de pico Uimp:	6 kV

The following current capacities have been verified by tests:

with fuses 63 A / 500 V (AC): 4x 63 A
with fuses 80 A / 690 V (AC): 4x 68 A

puntos de apriete
tunnel terminal 1.5 - 50 mm²

Cu: 1.5 - 50 mm² flexible with wire-end ferrule
Cu: 16 - 50 mm² stranded round
Cu: 1.5 - 10 mm² solid round

Al: 16 - 50 mm² solid round
Al: 50 mm² stranded sectored, pre-rounded 

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

cualidad de materiales
Cuerpo principal:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Brand 
Woehner or equivalent

Part No.
33777000A