Text for specification

Descripción
QUADRON^®60Classic
parte inferior de base NH de 160 A
borne-brida
talla 00/3P
60Classic

Normas
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

homologaciónes
IEC (CB), VDE, CCC

datos eléctricos
intensidad de corriente nominal (IEC):	160 A
tensión nominal (IEC) AC:	690 V
tensión nominal (IEC) DC:	440 V

power dissipation at full load of the item:	13,0 W
tensión de pico Uimp:	6 kV
tensión máxima (IEC) AC:	800 V
tensión máxima (IEC) DC:	800 V
corriente de cortocircuito cuando se protege por fusibles:	50 kA

Adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

puntos de apriete
Box terminal:
1.5 - 70 mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the lead 95 mm² could be connectable 
1.5 - 10 mm² solid round
16 - 70 mm² stranded round 
2x 10 mm², 2x 16 mm² and 2x 25 mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square 
2x 10 - 35 mm² flexible identical cables placed side by side

lam. Cu. 9 - 13 mm wide 
terminal space 13 mm x 13 mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

cualidad de materiales
Cuerpo principal:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contactos:
	spring-loaded copper contacts, silver plated 
Placa adaptadora:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Protección contra contacto:
	Resistencia a la temperatura hasta 125°C, 
	autoextintor según UL 94, 
	Resistencia a las corrientes de fuga CTI 200

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other

Brand 
Woehner or equivalent

Part No.
03199000