Text for specification

Descripción
AMBUS^®Panel
soporte para fusibles cilíndricos, con LED
Class CC / 3P
30 A / 600 V

Normas
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system J

homologaciónes
CSA, UL, CCC

datos eléctricos

intensidad de corriente nominal (UL):	30 A
tensión nominal (UL) AC:	600 V
tensión nominal (UL) DC:	600 V

power dissipation at full load of the item:	0,9 W

SCCR:	200 kA

indicator light
operating voltage range: 110 - 600 V AC / DC

puntos de apriete
for applications acc. to IEC / EN :
1 wire : 
Cu 0,75 - 25 mm²
2 wires (of same cross-section) :
Cu 0,75 - 10 mm² 
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E 60°C/75°C
1 wire : 
AWG 18 - AWG 8, Class B, Md 2,0 -2,5 Nm / 18 - 22 lb.in.
AWG 6 - AWG 4, Class C, Md 2,5 - 3,0 Nm / 22 - 26 lb.in.
2 wires (of identical cross-section) : 
AWG 18 - AWG 8, Class B, Md 2,0 - 2,5 Nm / 18 - 22 lb.in. 
AWG 6, Class C, Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

cualidad de materiales
Cuerpo principal:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Soporte de fusibles:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Tornillos de conexión:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range, also for two identical conductors (adjacent)
holder for label
with indicator for tripped fuse
any polarity for DC voltage

Brand 
Woehner or equivalent

Part No.
31300000