Text for specification

Descripción
CAPUS®Panel
seccionador con fusibles, 3 polos
tornillo M8, maneta roja
talla 00

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
IEC (CB)

datos eléctricos
intensidad de corriente nominal (IEC):	160 A
tensión nominal (IEC) AC:	690 V

AC-23A (690V/125A)
AC-23A (500V)
AC-22A (690V)
AC-21A (690V)

power dissipation at full load of the item:	28,0 W

tensión nominal de aislamiento Ui AC:	1000 V
tensión de pico Uimp:	8 kV

Mechanical lifespan (switching operations) 7000

conv. therm. current in housing
160 A, horizontal installation (adjacent poles) encapsulated 252 x 378 x 302mm
145 A, vertical installation (poles beneath each other) encapsulated 500 x 500 x 300mm

Shock protection at front with terminal space cover IP20

for fuse links DIN 43620 size 00 up to 12W power dissipation

puntos de apriete
Tornillo M8 :
Par de apriete 12,5 - 15,5 Nm

Miscellaneous 
double-breaking main contacts,
visible separation sections,
user-independent switching,
voltage-free exchange of fuses
assembly and connection material contained in scope of delivery.

Brand 
Woehner or equivalent

Part No.
33359000