Text for specification

Descripción
QUADRON^®185Power Speed
seccionador vertical NH, talla de fusible 00
modelo alto, conexión inferior M8
conexión CrossLink, con control de fusibles
185Power

- for vertical and horizontal mounting
- operator independent swichtching mechanism combined with linear operation kinematics
- disconnection of both sides of the NH-contacts (disconnection in front and after the NH-fuses)
- riskless mounting or demounting under voltage without personal protective equipment by using
  the touchprotected busbarsystem and CrossLink®Technology 
  (assessment of the german Employer's Liability Insurance Association)
- plug and play on the busbar system by sticking device with CrossLink-clamp or drilled 
  mounting
- flag indicator shows the switching state via red-green field
- lockable in OFF-position with max. three padlocks
- cover locking with a control panel key
- seal application in ON and OFF position
- all touchable parts are safe by opened cover
- impossible opening of the cover in ON position
- impossible mounting or demounting under load 
  (assessment of the german Employer's Liability Insurance Association)

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
IEC (CB)

datos eléctricos
intensidad de corriente nominal (IEC):	160 A
tensión nominal (IEC) AC:	400 V

AC-23B 160A/400V
AC-23B 160A/400V  

power dissipation at full load of the item:	55,0 W

tensión nominal de aislamiento Ui AC:	400 V
tensión de pico Uimp:	4 kV

The use of knife links is not permitted. The rated values specified in this product description apply exclusively to the use of fuses.

distance to grounded parts = 0mm at 120kA

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

cualidad de materiales
Caja:
	Resistencia a la temperatura hasta 130°C,
	autoextintor según UL 94,
	Resistencia a las corrientes de fuga CTI 600,
	Sin halógenos
Contactos:
	spring-loaded copper contacts, silver plated 
Tapa:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
When the cover is open, all touchable parts are voltage-free

Operator-independent switching

Lockable cover with double-bit lock

Mixed installation with all components 185Power

Can be sealed when switched on or off

Can be locked with up to 3 padlocks when switched off 

Brand 
Woehner or equivalent

Part No.
33624000A