Text for specification

Descripción
CRITO®
borne en pinza
Cu / Al 95 - 300 mm²
60Classic
100Energy
185mm-System
centre feed unit

Normas
IEC 61439-1:2020
IEC 60999-1:1999
IEC 60999-2:2003

homologaciónes
CSA, UL

datos eléctricos
intensidad de corriente nominal (IEC):	500 A
tensión nominal (IEC) AC:	690 V

intensidad de corriente nominal (UL):	420 A
tensión nominal (UL) AC:	600 V
máxima intensidad de corriente (IEC):	600 A
tensión máxima (IEC) AC:	1000 V
tensión máxima (IEC) DC:	1500 V

resistencia a corriente de pico Ipk máx. :	81,4 kA

SCCR: 65 kA with any DIVQ/7 circuit breaker 1200 A / 480 V AC 

puntos de apriete
for applications acc. to IEC / EN :
Cu 95 - 300 mm² stranded round cables and stranded sectored cables as well as flexible cables (directly)
Cu 240 - 300 mm² fine stranded flexible cables (directly)
Al 120 - 300 mm² stranded round cables and stranded sectored cables
Al 120 - 240 mm² solid sectored cables

for applications acc. to UL / CSA :
Cu 95 - 300 mm² / AWG 3/0 - MCM 600

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Brand 
Woehner or equivalent

Part No.
01760000