Text for specification

Descripción
CAPUS®Panel
interruptor-seccionador de 3 polos
tornillo M12, maneta gris grafito
800 A

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
IEC (CB)

datos eléctricos
intensidad de corriente nominal (IEC):	800 A
tensión nominal (IEC) AC:	500 V

AC-23B (500V)
AC-22B (500V)
AC-21B (500V)

power dissipation at full load of the item:	169,0 W

tensión nominal de aislamiento Ui AC:	1000 V
tensión de pico Uimp:	12 kV
capacidad de cerrar a cortocircuito:	40 kA

Mechanical lifespan (switching operations) 2500
rated short-circuit making capacity 40kA

conv. therm. current in housing
800A, horizontal installation (adjacent poles) encapsulated 756 x 378 x 482mm
800A, vertical installation (poles beneath each other) encapsulated 600 x 600 x 400mm

Shock protection at front with terminal space cover IP40

puntos de apriete
Tornillo M12 :
Par de apriete 36 - 44 Nm

Miscellaneous 
double-breaking main contacts, 
visible separation sections, 
user-independent switching, 
assembly and connection material contained in scope of delivery

Brand 
Woehner or equivalent

Part No.
33336000