Text for specification

Descripción
QUADRON^®185Power
seccionador vertical doble, 1250 A
tornillo M12, con cubierta del área de conexión incluida
3 polos conmutables
185Power

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

datos eléctricos
intensidad de corriente nominal (IEC):	1.250 A
tensión nominal (IEC) AC:	690 V

AC-20B (690 V)

DC-20B
max. voltage between the fuses: 800 V
visible information required: Do not switch under load.

power dissipation at full load of the item:	380,0 W

tensión nominal de aislamiento Ui AC:	1000 V
tensión de pico Uimp:	8 kV

version: connection bottom

ampacity with fuses NH3 gG 500 V AC 630 A:
- 1250 A bolt connection (it's recommended to wear gloves when operating)
- 1190 A bolt connection
- 1125 A using terminal clamp 33738 or 33740

ampacity with solid links (knives) 1000 A:
- 1550 A bolt connection
- 1350 A using terminal clamp 33738 or 33740 

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

Degree of protection IP20 at front, degree of protection near terminal depends on installation

puntos de apriete
screw M12 :
Md 30 Nm

Miscellaneous 
Self-closing inspection holes are available in the cover.

Cover can be locked when closed.

Brand 
Woehner or equivalent

Part No.
33731000A