Text for specification

Descripción
SECUR^®Panel
seccionador para fusibles D0 de hasta 63 A
con LED
3P

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
VDE

datos eléctricos
intensidad de corriente nominal (IEC):	63 A
tensión nominal (IEC) AC:	400 V
tensión nominal (IEC) DC:	130 V

AC-22B

power dissipation at full load of the item:	7,8 W

tensión nominal de aislamiento Ui AC:	500 V
tensión de pico Uimp:	6 kV

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638 : AC-22

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard.

There is a transfer of the potential from the busbars, through the LED units, to the terminals  when the fuse links are removed and the switching mechanismn is closed. 

puntos de apriete
box terminal :
1,5 - 35 mm²    flexible cables, directly or with wire-end ferrule
(flexible cables of maximum cross-section may not fit when using wire-end ferrule)
1,5 - 10 mm²    solid
Md 2,5 - 3 Nm

2 cables can be connected, when both chambers of the terminal are used
the maximum combination is 35mm² + 16mm²

cualidad de materiales
Caja:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Palanca:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Soporte de fusibles:
	temperature stability 150°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 125,
	halogen-free
Tornillos de conexión:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
Double function terminal
any feed direction
captive fuse-carrier
sealable operation

Brand 
Woehner or equivalent

Part No.
31557000A