Text for specification

Descripción
aislamiento del sistema, en la parte posterior
set para una separación en el soporte para barras de 550 mm (distancia entre ejes)
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Normas
IEC 61439-1:2011

homologaciónes
UL

datos eléctricos

cualidad de materiales
Cubierta:
	temperature stability 125°C,
	self-extinguishing in acc. to UL 94,
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
To safeguard against touching the busbars from behind.

Brand 
Woehner or equivalent

Part No.
01420000A