Text for specification

Descripción
soporte para barras universal
 
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Normas
IEC 61439-1:2011

homologaciónes
UL

datos eléctricos
tensión nominal (IEC) AC:	800 V
tensión nominal (UL) AC:	1000 V
tensión nominal (UL) DC:	1000 V

tensión nominal de aislamiento Ui AC:	1000 V
tensión de pico Uimp:	8 kV
tensión máxima (IEC) DC:	1500 V

resistencia a corriente de pico Ipk máx. :	106 kA

short-circuit capacity IEC / EN :
Ipk max. = 106 kA (busbars 120x10, 2 busbar supports in 550 mm distance)
go to calculation for  3-pole system (IEC) 

Brand 
Woehner or equivalent

Part No.
01430000A